THERMOMETER type MTVT 84

Description and general specifications

This instrument is designed to measure and control the temperature in oil filled distribution transformers and is made for outdoor mounting in as well tropical or arctical climates (ambient temperature range -40°C/+70°C). All components are made of corrosion resistant materials or surface treated materials.

This thermometer is fitted with 1 or 2 change-over (SPDT) microswitches working both normally open and normally closed (three terminals each microswitch) and is supplied with a junction board with 3 or 6 terminals + earth. Max. cable section = 2,5mm2.

TEMPERATURE SENSING SYSTEM : expansion type (liquid filled system), compensated for ambient temperature changing by means of a bimetallic spring.

CASING : aluminium alloy with powder painting high protection degree. On request case can be provided with an air breather device for ventilation.

PROTECTION DEGREE : IP 65.

MEASURING RANGE : -20/+ 120°C.

# SWITCHES MAKING AND BREAKING

CAPACITY (non inductive) : 5A       250V AC

250mA 250V DC

500mA 125V DC

INSULATION TEST : 2000V 50Hz between terminals and earth for a 60 secs. time.

MEASURING TOLERANCE : 1,5% of fsv.

COMMUTATION TOLERANCE : 2% of fsv.

| POS. | DESCRIPTION |
| --- | --- |
| 1 | Case |
| 2 | Cover |
| 3 | Connection |
| 4 | Bulb |
| 5 | Data plate |
| 6 | Cable gland |
| 7 | Switch setting knobs |
| 8 | Max temp indicating pointer |
| 9 | Breather device |

FINISHED PRODUCT QUALITY CONTROL TESTS

OIL TEMPERATURE INDICATOR

type MTVT 84

for distribution transformers

Instrument calibration : carried out through termostatic baths controlled by a computer system.

The procedure varies according to instruments scale.

The calibration procedure, being the thermometer scale :-20/+120°C :

is made using  5 different baths set at the following temperatures :

bath 1 = -20°C

bath 2 =  20°C

bath 3 =  50°C

bath 4 = 100°C

bath 5 = 115°C

Calibration procedure : Step 1: a check is carried out to see wheter the temperature taken by the instrument under test differs from that taken through the sample sensor by more than the 70% of the maximum allowed instrument reading tolerance value. This test  is performed  by  sequentially plunging  the TEMPERATURE INDICATOR bulb into successive  temperature  increasing thermostatic baths : -20°C/+20°C/+50°C/+100°C/+125°C

Step 2: the instrument is heated until the instrument pointer exceeds by 20% the angular full scale value.

Step 3: step 1 is repeated, but inversely.

Microswitches actuation test : performed through a computer controlled testing unit .

The bulb is immersed in a thermostatic bath. The computer changes the temperature inside the bath and by means of suitable sensors verifies the commutation tolerance, the commutation differential, the electrical circuits of each microswitch. At  the  end of the test a test report is directly printed by the computer.

Check of instrument mechanical protection degree : IP 65.

Isolation test : carried out by means of  a microprocessor controlled testing unit.

Note : all the collected data are immediately transferred, by means of the computer net, to the quality control  and to the design departments to be supervised and evaluated.

In our files, we keep all the above mentioned informations and, for each instrument, we can supply to the customer detailed reports regarding the performances of each instrument delivered.